# Smart Grid Sentinel: Real-World Optimization and Failure Analysis of IoT-Based Protection Systems

The implementation of high-fidelity electrical protection systems using low-cost, high-performance microcontrollers such as the ESP32 represents a paradigm shift in decentralized grid management. However, the transition from a theoretically sound design to a practically stable, industry-grade device requires an exhaustive understanding of the underlying physics governing electrical transients, thermodynamic constraints of industrial loads, and the inherent limitations of semiconductor-based sensing architectures. The Smart Grid Sentinel system, in its current iteration, exemplifies the "academic-to-industrial gap," where standard protection curves and thresholds fail to account for the volatile nature of inrush currents and the intricate sensitivities of appliances like air conditioners and induction motors. This report provides a comprehensive analysis of these failure modes and proposes a robust, multi-layered optimization strategy.

## Real-World Electrical Behavior of Industrial and Domestic Loads

To architect a reliable protection system, one must first deconstruct the electrical signatures of the loads being protected. The observed failures in the Smart Grid Sentinel—specifically the nuisance tripping of air conditioners and motors—are rooted in the physics of electromagnetic induction and mechanical inertia.

### The Physics of Motor Startup and Inrush Currents

When an induction motor is first energized, it operates under a condition known as "Locked Rotor" status. At the instant of contact closure, the rotor is stationary, which means the slip  is equal to 1. In this state, the motor behaves effectively like a transformer with a short-circuited secondary winding.1 Because the rotor is not yet turning, it cannot generate back electromotive force (EMF), which is the internal counter-voltage that normally opposes the applied line voltage during steady-state operation.3

Without back EMF, the current flowing through the stator windings is limited only by the motor's internal impedance, which consists of low static resistance and inductive reactance.4 This results in a transient surge known as Locked Rotor Amperage (LRA). The magnitude and duration of this surge are governed by several physical variables:

- Magnetic Inrush (The First Cycle): In the first half-cycle of energization, the current can spike to levels far exceeding the nominal LRA—sometimes reaching up to 20 times the rated load current.5 This is primarily due to the sudden establishment of the magnetic field and the potential for core saturation if the voltage is applied near the zero-crossing point.1

- Locked Rotor Current (The Acceleration Phase): Following the initial magnetic spike, the current settles into the LRA range, typically 5 to 8 times the Rated Load Amperes (RLA).8 This current persists as a plateau until the motor reaches approximately 70% to 80% of its synchronous speed.10

- Mechanical Load and Inertia: The duration of the startup transient is directly proportional to the mechanical inertia of the load. A lightly loaded fan may reach steady state in 100-250 milliseconds, whereas a high-pressure pump or a central air conditioning compressor may remain in the inrush phase for several seconds.8

The following table summarizes the typical startup characteristics that the Smart Grid Sentinel must accommodate to avoid nuisance trips.

| Appliance Type | Inrush Multiple (x RLA) | Duration (Typical) | Critical Constraint |
| --- | --- | --- | --- |
| Central Air Conditioner |  | seconds | Head pressure equalization 8 |
| Refrigerator Compressor |  | seconds | Starting torque requirements 9 |
| Induction Motor (DOL) |  | seconds | Slip-dependent impedance 8 |
| LED Lighting/SMPS |  | milliseconds | Input capacitor charging 15 |
| Toroidal Transformers |  | milliseconds | Core saturation physics 1 |

### The Causal Link Between Environment and Inrush Magnitude

The Smart Grid Sentinel must account for the fact that inrush current is not a static value. For example, the resistance of copper windings has a positive temperature coefficient. On a cold day, the windings have lower resistance, which can lead to significantly higher inrush peaks than those measured at room temperature.17 Furthermore, if the system has been recently de-energized, residual magnetism in the cores of transformers or motors can either subtract from or add to the required flux during the next start. If the residual flux and the new applied voltage have additive polarities, the resulting saturation leads to a "worst-case" inrush event.1

### Differentiating Between Inrush and Short Circuits

A critical failure in the current Sentinel implementation is the "Instant Trip" (27A) overriding the blanking window. This logic fails to distinguish between a healthy startup surge and a catastrophic short circuit. Industry-grade systems utilize waveform analysis to make this distinction:

- Decay Profile: Inrush current is characterized by a gradual, exponential decay as the rotor accelerates and back EMF increases.18 A short circuit current, however, remains at a high, sustained level until the protection device clears the fault or the wiring fails.7

- Harmonic Signature: Transformer inrush is notoriously rich in the second harmonic (100Hz in a 50Hz system), often representing 30% to 70% of the fundamental frequency component.7 Genuine fault currents are predominantly fundamental frequency sine waves with very low harmonic content.7

- Phase Asymmetry: Inrush currents are often highly asymmetrical during the first few cycles, shifting the entire waveform offset from the zero-axis.18 While faults can also be asymmetrical depending on the phase angle of inception, the persistence of the offset in inrush waveforms is a unique identifier used by digital relays.7

## Industry Protection Practices and Standards

To solve the nuisance tripping issues while maintaining a high safety factor, the Smart Grid Sentinel must adopt the graded protection strategies used in Miniature Circuit Breakers (MCBs) and industrial protective relays.

### MCB Tripping Curves (IEC 60898-1)

Industry standards categorize MCBs into B, C, and D curves based on the threshold of their instantaneous magnetic trip mechanism. Each curve is designed to "ride through" specific levels of inrush current while still providing thermal protection against sustained overloads.21

| Curve Type | Magnetic Trip Threshold | Ideal Application | Suitability for AC/Motors |
| --- | --- | --- | --- |
| Type B |  | Resistive loads (heaters, lighting) | Poor; prone to nuisance trips 23 |
| Type C |  | Mixed loads, small motors, fans | Moderate; suits standard motors 25 |
| Type D |  | Heavy industrial motors, transformers | Excellent; handles high LRA 23 |

In the Sentinel’s current configuration, a 16A rated system with a 27A instant trip is effectively operating on a threshold of . This is significantly more sensitive than even a Type B curve (). For an air conditioner with an LRA of 90A, the instant trip must be set above 90A (or approximately ) to permit startup.26

### Industrial Relay Logic: ANSI 50 and 51

Commercial protection relays (like those from SEL or ABB) do not use a single "trip if " logic. They utilize a multi-stage approach defined by ANSI codes:

- ANSI 51 (Time Overcurrent): This follows an Inverse Definite Minimum Time (IDMT) curve. It provides thermal protection for the conductors and the load. As the current increases, the time to trip decreases.27 This is the Sentinel's primary defense against continuous overloads ( to ).

- ANSI 50 (Instantaneous Overcurrent): This is divided into "Low-set" and "High-set" elements.

  - Low-set 50: Set slightly above the peak operating current (e.g., ). This element is blocked or restrained during the motor startup window.7

  - High-set 50 (Unrestrained): This is set above the maximum possible LRA (e.g., ). It is always active and provides instantaneous clearing for real short circuits, even during the startup phase.30

### IDMT Tuning Best Practices

The IEC 60255 standard defines several curve shapes. For motor protection, an "Extremely Inverse" curve is often preferred as it closely matches the thermal damage curve of motor windings.28 The trip time is calculated using the following LaTeX equation:

Where  is the Time Multiplier Setting,  is the actual current, and  is the pickup current. For motor protection, the Sentinel should tune  to approximately 115-125% of the motor’s FLA.32

## The Instant Trip vs. Inrush Conflict: A Logical Failure Analysis

The Sentinel’s current logic—where a 27A instant trip remains active during a 3.5-second blanking window—is structurally flawed. This section analyzes the conflict and provides the necessary design patterns to resolve it.

### Why the Current Logic Fails

The "blanking window" is intended to ignore the IDMT curve during startup to prevent slow thermal trips. However, if the "Instant Trip" is set at 27A, it acts as a hard ceiling. Since the AC unit draws 30A-90A during startup, the system will always trip instantly, rendering the blanking window and  slope detection useless.34 In effect, the system is trying to protect a 90A transient event with a 27A fuse.17

### Industry Design Patterns for Startup Handling

To resolve this, the Sentinel must implement one of three standard industry patterns:

#### 1. Inrush Restraint (Adaptive Multiplier)

Instead of disabling the instant trip, the system applies a temporary multiplier to the threshold during the startup window. If the normal trip is 27A, the system could multiply this by  for the first 2 seconds, effectively raising the threshold to 108A.35 This keeps the system "short-circuit aware" while allowing the 90A surge to pass.

#### 2. Harmonic Restraint Blocking

The system performs a Fast Fourier Transform (FFT) on the current samples. If the ratio of the 2nd harmonic to the fundamental component exceeds a threshold (typically 15-20%), the relay identifies the surge as an inrush condition and blocks the low-set instantaneous trip.7 Tripping is only permitted if the high-set unrestrained threshold is breached, indicating a fault that even harmonics cannot mask.20

#### 3. Motor Starting State Machine

This is the most sophisticated approach. The system maintains a state variable:

- IDLE: Current  (e.g., 0.5A).

- STARTING: Current rises above . Thresholds are raised to . Timer  begins.

- RUNNING: Current drops below  OR  expires. Thresholds revert to sensitive values (16A/27A).

- FAULT: Current . Immediate trip in any state.

## Reclose Delay and Compressor Safety: The Thermodynamics of Failure

The current Sentinel reclose delay of 5 seconds is arguably the most dangerous aspect of its operation for appliances involving refrigeration cycles. Attempting to restart a compressor within seconds of a shutdown can lead to permanent mechanical and electrical failure.

### The 3-Minute Rule and Thermodynamic Equilibrium

A refrigeration system works on the vapor-compression cycle, maintaining high-pressure refrigerant in the condenser and low-pressure refrigerant in the evaporator.39 When the compressor stops, these pressures are highly unbalanced.41 It takes approximately 3 to 5 minutes for the refrigerant to bleed through the metering device (expansion valve or capillary tube) and equalize throughout the system.41

### Consequences of Early Reclosing

- High Starting Torque/Locked Rotor: If the compressor tries to start against high residual head pressure, the motor must overcome a massive mechanical resistance. This is akin to trying to pedal a bicycle uphill while in the highest gear.43 The motor fails to turn and remains in the LRA state, drawing 90A and generating intense heat until a protection device trips.42

- Liquid Slugging: During an immediate restart, the rapid pressure fluctuations can cause liquid refrigerant (rather than vapor) to enter the compressor's suction port. Since liquids are non-compressible, this results in "slugging," which can shatter internal valves, pistons, or the orbiting scrolls in high-efficiency units.41

- Winding Degradation: Every time the motor enters a "failed start" cycle, the windings experience  heating that is  times higher than normal.5 This degrades the enamel shellac insulation on the wires, eventually leading to inter-turn shorts or a ground fault.5

### Implementation of Anti-Short-Cycle Protection

The Sentinel's reclose logic must be updated to a "Delay on Break" (DOB) timer. In this logic, the moment the relay is opened (whether by a fault or a command), a lockout timer of 180 seconds is initiated.48 Any attempt to reclose—even if the voltage and current return to normal—must be blocked until the timer expires.42

| Parameter | Recommended Value | Reasoning |
| --- | --- | --- |
| First Reclose Delay | 180 seconds | Minimum time for refrigerant pressure equalization 41 |
| Second Reclose Delay | 600 seconds | Allows cooling of windings after a failed start 51 |
| Consecutive Starts Limit | 3 starts per hour | Prevents thermal cumulative stress on insulation 32 |
| Reclose Hysteresis |  | Ensures grid stability before attempting reconnection 53 |

## Solving ADC Non-Linearity: Mastering the ESP32 SAR ADC

The Smart Grid Sentinel's misdetection of overvoltage conditions is primarily caused by the inherent inaccuracies of the ESP32’s internal Analog-to-Digital Converter (ADC). The 12-bit SAR ADC is not a precision measurement tool in its default state.

### Why the ESP32 ADC is Non-Linear

The non-linearity of the ESP32 ADC is well-documented and stems from three primary sources:

- The Dead Zone: At the bottom end of the range, even with no attenuation, the ADC cannot resolve voltages below approximately 100mV. With the standard 11dB attenuation, this "dead zone" extends to nearly 200mV.54

- Saturation/Clipping: At the top end, the ADC begins to saturate and lose linearity well before the 3.3V rail. Typically, the response curve flattens out around 2.45V to 2.6V.54

- Reference Voltage Variance: The internal reference voltage  is nominally 1100mV, but in production, it can range from 1000mV to 1200mV across different chips.56 Without individual calibration, this creates a systematic gain error of up to 10%.58

### Practical Correction Techniques for Embedded Measurement

To achieve professional-grade accuracy with the ZMPT101B voltage sensor, the Sentinel must implement one of the following software-based correction frameworks.

#### 1. Polynomial Regression Correction

A 3rd-order polynomial provides an excellent fit for the ESP32's non-linear "S-curve." Research indicates that using 3rd-order regression can reduce voltage measurement error to less than 1% across a wide range of AC inputs.59 The conversion follows the formula:

The coefficients  must be derived by correlating raw ADC samples against a trusted multimeter reading during a one-time calibration phase.59

#### 2. Density-Optimized Lookup Tables (LUT)

The most efficient method for a microcontroller is a LUT combined with piecewise linear interpolation. Instead of a uniform table, a "density-optimized" approach places 65% of the calibration points in the critical mid-range (0.5V to 2.5V) where the non-linearity is most severe.61 This method requires only about 264 bytes of memory and provides a measurement processing time of 2.3ms.61

#### 3. ESP-IDF Calibration API

Espressif provides a native calibration driver (esp_adc_cal.h) that reads factory-burned calibration values from the chip's eFuse.56 Utilizing esp_adc_cal_raw_to_voltage() can improve error from  to  without any additional hardware.54

### Hardware Optimization for Sensing Accuracy

Beyond software, the physical sensing circuit must be optimized to provide the best signal to the ADC:

- Voltage Divider Scaling: Design the divider or adjust the ZMPT101B potentiometer so that the maximum expected AC peak (e.g., 253V RMS  peak) maps to exactly 2.0V at the ADC pin. This ensures the entire signal remains within the "fairly linear" 0.15V-2.45V zone.54

- Input Buffering: The ESP32 ADC has a relatively low input impedance (). Directly connecting high-impedance sensors will cause the voltage to sag. Using an operational amplifier as a voltage follower buffer is essential for accurate readings.54

- Oversampling and Averaging: To mitigate switching noise and Wi-Fi radio interference, the system should take multiple readings (e.g., 64 samples) quickly and average them. This reduces random noise by a factor of .54

## System Design Improvements: From Prototype to Professional Grade

The following design changes will transform the Smart Grid Sentinel into a resilient, industry-grade protection system.

### Correct Current Protection Architecture

The current SCT-013 current transformer must be paired with a burden resistor that allows the system to see the 90A LRA peak without clipping the ADC input.

- Logic: Implement two "Instantaneous" thresholds.

  - Low-Set Instant: 27A. Active only when the system is in the "RUNNING" state.

  - High-Set Instant: 120A. Active in all states to catch short circuits.29

- Sampling: Use a True RMS calculation algorithm over exactly 1 AC cycle (20ms for 50Hz). Avoid using "peak-to-peak" as it is too sensitive to noise spikes.53

### Multi-Variable Fault Classification Logic

The Sentinel should not treat every trip as a simple "overcurrent" event. It must classify the failure to provide actionable diagnostics and safe reclosing paths.

| Fault Signature | Classification | Recommended Logic |
| --- | --- | --- |
| Current for | Short Circuit | Immediate trip. Permanent lockout. Requires manual reset.34 |
| Current for | Locked Rotor | Trip. Reclose after 180s. Log as "Mechanical Stall".52 |
| Current for | Thermal Overload | Trip according to IDMT curve. Reclose after 300s.28 |
| Voltage for | Grid Brownout | Trip. Reclose when after 180s DOB timer.43 |
| Voltage for | Surge/Grid Fault | Immediate trip. Reclose when after 180s DOB timer.41 |

### Advanced Inrush Strategy: The "Three-S" Approach

- Slope (di/dt) Detection: During the first cycle, if current is high but the rate of change is decreasing, it is likely a healthy magnetizing surge.67

- Symmetry Analysis: Check for the characteristic unipolar offset of motor inrush. If present, temporarily desensitize the 27A threshold.18

- Start-up Duration: If the current does not drop below the pickup threshold within the defined  (e.g., 3.5s), the load is failing to accelerate, and the system must trip to prevent burnout.52

### Pseudocode for Motor Startup Supervision and Restart Inhibition

C++

// Constants and Variables
const float I_IDLE_LIMIT = 0.5; // Amps
const float I_STARTUP_LIMIT = 90.0; // Amps for LRA
const float I_NOMINAL_LIMIT = 16.0; // Amps RLA
const int T_START_MAX = 3500; // 3.5 seconds in ms
const int T_LOCKOUT_DOB = 180000; // 180 seconds rule

enum SystemState { IDLE, STARTING, RUNNING, FAULT_LOCKOUT };
SystemState currentState = IDLE;
unsigned long stateTimer = 0;
unsigned long lockoutTimer = 0;

void protectionLoop() {
  float currentAmps = getTrueRMSCurrent();
  float voltageRMS = getCalibratedVoltage();

  // 1. Critical Hard-Short Check (Always Active)
  if (currentAmps > 120.0) {
    tripRelay();
    currentState = FAULT_LOCKOUT;
    return;
  }

  // 2. Anti-Short Cycle Lockout Logic
  if (lockoutTimer > 0 && millis() < lockoutTimer) {
    relayOff();
    return;
  }

  switch (currentState) {
    case IDLE:
      if (currentAmps > I_IDLE_LIMIT) {
        currentState = STARTING;
        stateTimer = millis();
        // Set higher threshold during startup
        setInstantTripThreshold(100.0); 
      }
      break;

    case STARTING:
      // Check for successful acceleration
      if (currentAmps < (I_NOMINAL_LIMIT * 1.2)) {
        currentState = RUNNING;
        setInstantTripThreshold(27.0); // Sensitive protection
      } 
      // Check for prolonged startup (Locked Rotor)
      else if (millis() - stateTimer > T_START_MAX) {
        tripRelay();
        initiateLockout(T_LOCKOUT_DOB);
        currentState = IDLE;
      }
      break;

    case RUNNING:
      // Normal protection logic
      if (currentAmps > 27.0) {
        tripRelay();
        initiateLockout(T_LOCKOUT_DOB);
        currentState = IDLE;
      }
      // Check for motor stop
      if (currentAmps < I_IDLE_LIMIT) {
        currentState = IDLE;
        initiateLockout(T_LOCKOUT_DOB);
      }
      break;
  }
}

void initiateLockout(long duration) {
  relayOff();
  lockoutTimer = millis() + duration;
}

## Summary of Optimization Parameters

To achieve an industry-grade system, the following parameters should be integrated into the Sentinel's configuration:

- Undervoltage Trip: 207V with a 5-second definite-time delay to allow for local grid recovery from the appliance’s own inrush.46

- Overvoltage Trip: 253V with a 200ms delay to protect against utility surge transients.41

- Instant Trip (Run State): 27A - 48A ( to ).23

- Instant Trip (Start State): 110A () to accommodate the 90A LRA.8

- IDMT Pickup: 20A () following an IEC Extremely Inverse curve for winding protection.29

- Reclose DOB Delay: 180 seconds (3-minute rule) for compressor health.41

- ADC Logic: 3rd-order polynomial calibration + Op-amp buffer for sub-1% voltage accuracy.59

## Final Conclusion

The transition of the Smart Grid Sentinel from a theoretical prototype to a production-ready device requires a rigorous commitment to the physical constraints of both the load and the sensing hardware. The observed startup failures are not faults of the appliances, but rather the failure of the protection logic to respect the  inrush multiples inherent in induction motor physics. By replacing the sensitive, single-stage 27A trip with a tiered, state-aware overcurrent architecture, the Sentinel can maintain protection against dead-shorts without sacrificing operational continuity. Furthermore, the mandatory implementation of a 180-second "Delay on Break" timer ensures that high-value compressors are never subjected to the catastrophic mechanical stress of an un-equalized restart. Finally, addressing the non-linearities of the ESP32 ADC through 3rd-order polynomial regression and density-optimized lookup tables provides the measurement precision necessary for the system to act as a reliable guardian of grid health. These industry-standard enhancements transform the Smart Grid Sentinel into a resilient, appliance-safe protection platform.

#### Works cited

- Inrush current - Wikipedia, accessed on April 17, 2026, https://en.wikipedia.org/wiki/Inrush_current

- Induction Motor, Inrush Current vs. Locked Rotor Current - CR4 Discussion Thread, accessed on April 17, 2026, https://cr4.globalspec.com/thread/60035/Induction-Motor-Inrush-Current-vs-Locked-Rotor-Current

- ¿What is a Locked Rotor Amperes and how does it work? - Area Cooling Solutions, accessed on April 17, 2026, https://areacooling.com/hvac-glossary/locked-rotor-amperes/

- What You Know About Start Winding Inrush Current Might Be Wrong - HVAC School, accessed on April 17, 2026, http://www.hvacrschool.com/what-you-know-about-start-winding-inrush-might-be-wrong/

- Motor Starting Currents | Eaton, accessed on April 17, 2026, https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-motor-starting-currents.pdf

- MOTOR TRIP ON RUSH CURRENT - Mike Holt's Forum, accessed on April 17, 2026, https://forums.mikeholt.com/threads/motor-trip-on-rush-current.2573170/

- Transformer Inrush Current & Nuisance Trips: Prevention Guide - XBRELE, accessed on April 17, 2026, https://xbrele.com/transformer-inrush-current-nuisance-trips-prevention/

- Free Motor Starting Current Calculator — Inrush | FIRGELLI Engineering, accessed on April 17, 2026, https://www.firgelliauto.com/blogs/engineering-calculators/motor-starting-current-calculator-inrush

- Induction Motors and Their Impact on Power Systems - AllumiaX Engineering, accessed on April 17, 2026, https://www.allumiax.com/blog/induction-motors-and-their-impact-on-power-systems

- Can someone please explain inrush current? : r/HVAC - Reddit, accessed on April 17, 2026, https://www.reddit.com/r/HVAC/comments/7p6obb/can_someone_please_explain_inrush_current/

- Start 'Em Up! - Coastal Climate Control, accessed on April 17, 2026, https://coastalclimatecontrol.com/blog/start-em-up-marine-air-conditioning-1

- Can Your Battery Start the AC? | LRA, Surge Power & Inverter Matching Guide - EcoFlow, accessed on April 17, 2026, https://www.ecoflow.com/us/blog/battery-start-air-conditioner-guide

- Compressor LRA is the same as RLA? : r/hvacadvice - Reddit, accessed on April 17, 2026, https://www.reddit.com/r/hvacadvice/comments/1krevql/compressor_lra_is_the_same_as_rla/

- Motor inrush current | Megger, accessed on April 17, 2026, https://www.megger.com/en-ca/et-online/april-2022/motor-inrush-current

- What Is Inrush Current? A Buyer's Guide to Electrical Spikes, accessed on April 17, 2026, https://www.commercial-lighting.net/what-is-inrush-current/

- What is Inrush Current and Peak Current? - Pacific Power Source, accessed on April 17, 2026, https://pacificpower.com/inrush-current-and-peak-current/

- Inrush Current 101: How to Tame the Power-On Spike - EcoFlow, accessed on April 17, 2026, https://www.ecoflow.com/us/blog/what-is-inrush-current

- What Is Transformer Inrush Current and How Is It Managed?, accessed on April 17, 2026, https://taishantransformer.com/transformer-inrush-current-management/

- Understanding Sympathetic Inrush Currents and Their Effect on Protective Relays | WPRC-Archives, accessed on April 17, 2026, https://wprcarchives.org/wp-content/uploads/2024/04/Holbach_Juergen_Understanding-Sympathetic-Inrush-Currents-and-Their-Effect-on-Protective-Relays_2012.pdf

- Considerations for Using Harmonic Blocking and Harmonic Restraint Techniques on Transformer Differential Relays | WPRC-Archives, accessed on April 17, 2026, https://wprcarchives.org/wp-content/uploads/2024/07/Ken-Behrendt_Considerations-for-Using-Harmonic-Blocking-and-Harmonic-Restraint-Techniques-on-Transformer-Differential-Relays_2006.pdf

- — What you need to know about miniature circuit breaker trip curves - ABB, accessed on April 17, 2026, https://library.e.abb.com/public/b5acf03b2a1f42e3b08ed2fc27672c30/What+you+need+to+know+about+MCB+trip+curves.pdf?x-sign=V1sNgpc4uKO3vqAeyV7a2HP1A8UTmxUOGgvA3xuldqD7t7CV5AcB4Whn6K6wTOcO

- Tripping curves - Tekdok.dk, accessed on April 17, 2026, https://www.tekdok.dk/files/CA908024E_Trip_curve_2021.pdf

- Circuit Breaker Trip Curves (B, C, D): 2025 Guide, accessed on April 17, 2026, https://breakerhunters.com/blogs/news/circuit-breaker-trip-curves-b-c-d-2025-guide

- MCB Tripping Curves – Types B, C, D, K, Z & Characteristics | ElectGo, accessed on April 17, 2026, https://electgo.com/resources/mcb-trip-mcb-connection

- Guide to MCB Trip Curves: Selecting the Right B, C, or D Curve for Overcurrent Protection, accessed on April 17, 2026, https://www.chintglobal.com/global/en/about-us/news-center/blog/guide-to-mcb-trip-curves--selecting-the-right-b--c--or-d-curve-f.html

- Type A, B, C and D Miniature Circuit Breakers: What Are the Differences - ELEHUB, accessed on April 17, 2026, https://elehub.com/type-a-b-c-d-miniature-circuit-breakers/

- IEC 60255 Relay Tripping Curves Explained | PDF | Technology & Engineering - Scribd, accessed on April 17, 2026, https://www.scribd.com/doc/126772136/Tripping-Curves

- Instantaneous and Time-overcurrent (50/51) Protection | Electric Power Measurement and Control Systems | Textbook, accessed on April 17, 2026, https://control.com/textbook/electric-power-measurement-and-control/instantaneous-and-time-overcurrent-5051-protection/

- M-3310 Relay Settings: Inrush, Instantaneous, 51 & 46 Elements - Industrial Monitor Direct, accessed on April 17, 2026, https://industrialmonitordirect.com/blogs/knowledgebase/beckwith-m-3310-relay-configuration-for-generator-transformer-units

- Explain "instantaneous override" and "close and latch" ratings | Schneider Electric USA, accessed on April 17, 2026, https://www.se.com/us/en/faqs/FA237963/

- New Inrush Stability Algorithm Improves Transformer Protection - Schweitzer Engineering Laboratories, accessed on April 17, 2026, https://selinc.com/api/download/122500/

- Motor Protection Theory - GE Vernova, accessed on April 17, 2026, https://www.gevernova.com/grid-solutions/sites/default/files/2024-12/motor%20protection%20theory.pdf

- Types and Applications Of Overcurrent Relay | EEP - Electrical Engineering Portal, accessed on April 17, 2026, https://electrical-engineering-portal.com/types-and-applications-of-overcurrent-relay-1

- Switchgear Trips Immediately After Closing | Protection or Mechanical Fault?, accessed on April 17, 2026, https://r-aletqan.medium.com/switchgear-trips-immediately-after-closing-protection-or-mechanical-fault-0f741f0fc919

- What is Inrush Restraint? | NOJA Power - Recloser Switchgear Engineers, accessed on April 17, 2026, https://www.nojapower.com.au/expertise/2021/what-is-inrush-restraint

- Section 5 Protection related functions, accessed on April 17, 2026, https://na.eventscloud.com/file_uploads/947b0fc0302067be7243ce465996569a_ABBREF615-3b.pdf

- Inrush Restraint for Transformer Differential Protection with Current Waveform Analysis (CWA) in SIPROTEC 4 7UT6x - HV Power, accessed on April 17, 2026, https://hvpower.co.nz/cms/assets/7d3bac6c-9c62-4829-8fb2-03aad02ee4de

- Review of Protection Approaches for Discrimination between Internal Fault and Inrush Current in Electric Power Transformers, accessed on April 17, 2026, https://aast.edu/pheed/staffadminview/pdf_retreive.php?url=70665_45_49_Review%20of%20Protection%20Approaches%20for%20Discrimination%20between%20Internal%20Fault%20and%20Inrush%20Current%20in%20Electric%20Power%20Transformers.pdf&stafftype=staffpdf

- Second law of thermodynamics - Simple English Wikipedia, the free encyclopedia, accessed on April 17, 2026, https://simple.wikipedia.org/wiki/Second_law_of_thermodynamics

- How an Air Conditioner Works | The Refrigeration Cycle - Service Champions, accessed on April 17, 2026, https://www.servicechampions.net/blog/air-conditioner-works-refrigeration-cycle

- The 3-Minute Rule for Air Conditioners — What It Is | Berkeys Fort Worth, accessed on April 17, 2026, https://www.berkeys.com/fort-worth/air-conditioning/resources/what-is-the-3-minute-rule-for-air-conditioners-and-why-does-it-matter/

- What is the 3 Minute Rule for Air Conditioners? - ClimateWorks, accessed on April 17, 2026, https://www.climateworks.co.uk/post/what-is-the-3-minute-rule-for-air-conditioners

- What Is the 3-Minute Rule for AC? - Cowboys AC - HVAC San Antonio, accessed on April 17, 2026, https://cowboysac.com/what-is-the-3-minute-rule-for-ac/

- What Is the 3-Minute Rule for Air Conditioners and Why It Can Save You a Costly Repair, accessed on April 17, 2026, https://altruisticac.com/what-is-the-3-minute-rule-for-air-conditioners-and-why-it-can-save-you-a-costly-repair/

- Inrush Current (Full Lecture) - YouTube, accessed on April 17, 2026, https://www.youtube.com/watch?v=3ikIPOnBLtY

- What Is Inrush Current? Causes, Effects on Breakers & Calculation - VIOX Electric, accessed on April 17, 2026, https://viox.com/what-is-inrush-current/

- How exactly does short cycling damage a compressor? : r/HVAC - Reddit, accessed on April 17, 2026, https://www.reddit.com/r/HVAC/comments/1nexzhu/how_exactly_does_short_cycling_damage_a_compressor/

- Anti-Short-Cycle - Airotronics Timers and Controls, accessed on April 17, 2026, https://www.airotronics.com/products-antishortcycle.php

- ON DELAY VS OFF DELAY TIMERS: Complete Technical Comparison Guide (2026), accessed on April 17, 2026, https://viox.com/on-delay-vs-off-delay-timers/

- Anti-short cycle delay - PENN Controls - LIT-12011972 - A421GBF - A421AEC, accessed on April 17, 2026, https://docs.johnsoncontrols.com/bas/r/PENN-Controls/en-US/A421-Series-Standard-Electronic-Temperature-Controls-with-and-without-Power-Cords-Product-Bulletin/Anti-short-cycle-delay

- HVAC Short Cycling: Causes and Solutions - Trane®, accessed on April 17, 2026, https://www.trane.com/residential/en/resources/glossary/hvac-short-cycling/

- Motor Start-up Supervision - Protecta, accessed on April 17, 2026, https://www.protecta.hu/files/files/42117/mss48_v2.0.pdf

- "Unlocking Success: AC Voltage Measurement With ESP32" - iotwebplanet, accessed on April 17, 2026, https://iotwebplanet.com/ac-voltage-measurement-with-esp32/

- ESP32 ADC Accuracy: Fix Noise and Non-Linearity Issues - Zbotic, accessed on April 17, 2026, https://zbotic.in/esp32-adc-accuracy-fix-noise-and-non-linearity-issues/

- Fixing the non linear ADC of an ESP32 - General Guidance - Arduino Forum, accessed on April 17, 2026, https://forum.arduino.cc/t/fixing-the-non-linear-adc-of-an-esp32/699190

- e-tinkers/esp32-adc-calibrate - GitHub, accessed on April 17, 2026, https://github.com/e-tinkers/esp32-adc-calibrate

- Analog to Digital Converter - ESP32 - — ESP-IDF Programming Guide v4.2 documentation, accessed on April 17, 2026, https://docs.espressif.com/projects/esp-idf/en/v4.2/esp32/api-reference/peripherals/adc.html

- Density-Optimized Lookup Table with Piecewise Linear Interpolation for ESP32 ADC Precision Enhancement - ResearchGate, accessed on April 17, 2026, https://www.researchgate.net/publication/403529468_Density-Optimized_Lookup_Table_with_Piecewise_Linear_Interpolation_for_ESP32_ADC_Precision_Enhancement

- (PDF) CALIBRATION OF ZMPT101B VOLTAGE SENSOR MODULE USING POLYNOMIAL REGRESSION FOR ACCURATE LOAD MONITORING - Academia.edu, accessed on April 17, 2026, https://www.academia.edu/35436923/CALIBRATION_OF_ZMPT101B_VOLTAGE_SENSOR_MODULE_USING_POLYNOMIAL_REGRESSION_FOR_ACCURATE_LOAD_MONITORING

- (PDF) Calibration of ZMPT101B voltage sensor module using polynomial regression for accurate load monitoring - ResearchGate, accessed on April 17, 2026, https://www.researchgate.net/publication/316636029_Calibration_of_ZMPT101B_voltage_sensor_module_using_polynomial_regression_for_accurate_load_monitoring

- Density-Optimized Lookup Table with Piecewise Linear Interpolation for ESP32 ADC Precision Enhancement, accessed on April 17, 2026, https://ejournal.unibabwi.ac.id/index.php/Zetroem/article/download/7602/4704

- Density-Optimized Lookup Table with Piecewise Linear Interpolation for ESP32 ADC Precision Enhancement, accessed on April 17, 2026, https://ejournal.unibabwi.ac.id/index.php/Zetroem/article/download/7602/4704/50194

- What is the difference between a low set and high set relay? - Gozuk, accessed on April 17, 2026, http://www.gozuk.com/forum/what-is-the-difference-between-a-low-set-and-high-set-relay-466475.html

- ESPHome ZMPT101B Sensor - GitHub, accessed on April 17, 2026, https://github.com/hugokernel/esphome-zmpt101b

- Short-Circuit Protection or Overload Protection - Electrical Equipment Company, accessed on April 17, 2026, https://eecoonline.com/inspire/short-circuit-protection-or-overload-protection

- Relay Setting in Real Power System - AllumiaX Engineering, accessed on April 17, 2026, https://www.allumiax.com/blog/relay-settings-in-real-power-system

- US20090147412A1 - Transformer inrush current detector - Google Patents, accessed on April 17, 2026, https://patents.google.com/patent/US20090147412A1/en

- DIGITAL DIFFERENTIAL RELAY FOR ELECTRICAL POWER TRANSFORMER اﻟﻤﻠﺨص . ﻫذا ﺎﺌ ﺔ اﻟﻛﻬر اﻟﻘد, accessed on April 17, 2026, https://jer.ly/PDF/Vol-23-2017/JER-01-23.pdf